## AirGap
AIR GAP MEASURING CHAINS | [14 empty] | Project: | [6 empty] | Unit:
[12 empty] | Service nb : | [6 empty] | Service nb :
Item | Position | WME | OUT OF BOX | [8 empty] | AT INSTALLATION | [6 empty] | AT ZOOM CABINET
|  |  | VM Sensor |  |  |  | Triaxial |  | LIN |  | Functional test | Current | Capacitance |  | Grounding |  |  | Shim | Signal Cable |  | ZPU |  |  | Current | ZOOM | Status | ZOOM CONFIG
[13 empty] | Triaxial /Sensor |  | (Ω) |  |  |  | Cable TAG | Shield connected at (M12 / TB)
(nF)
|  |  | Slot # | Angle | Serial Number | VSM PRODUCT NUMBER | Serial Number | VSM PRODUCT NUMBER | Serial Number | VSM PRODUCT NUMBER | 1. Triaxial impedance 2. LIN status LED 3. Current output variation | Output (mA) | Core / Inner Shield | Core / Tab | Stator Frame |  | Shield Inner / Outer |  |  |  | ID | Ch # | Input Module | Output (mA) | Air Gap
[15 empty] | LIN | Tab
1
2
3
4
5
6
7
8
9
10
11
12
Limits & Measuring Method
General | [21 empty] | Limits |  |  | Tool
Item |  |  | Sequential number | [18 empty] | N/A |  |  | N/A
Unit |  |  | Unit number on which the sensor is installed | [18 empty] | N/A |  |  | N/A
Position |  |  | Top, Middle or Bottom | [18 empty] | N/A |  |  | N/A
WME |  |  | Sensor is wired to this junction box. | [18 empty] | N/A |  |  | N/A
VSM PRODUCT NUMBER |  |  | All VSM numbers in order to verify compatibility. | [18 empty] | N/A |  |  | N/A
Out of the Box | [21 empty] | Limits |  |  | Tool
Serial Number |  |  | Sensor serial number | [18 empty] | N/A |  |  | N/A
Slot |  |  | As per calculations / review with customer | [18 empty] | N/A |  |  | N/A
Angle |  |  | Calculated from slot location | [18 empty] | N/A |  |  | N/A
Functional test |  |  | 1. Measure continuity from inner shield to outer shield of the triaxial cable 2. Connect sensor-cable-LIN, power the LIN with 24Vdc and verify the LED status 3. Move your hand in front of the sensor and verify the output current variation | [18 empty] | Open Green 4 to 20 mA |  |  | 24Vdc PS Fluke meter
At Installation | [21 empty] | Limits |  |  | Tools
mA |  |  | Measure the signal output from LIN module and record value. | [18 empty] | Min 4 mA +0/-0.5 |  |  | Fluke meter
Max 20 mA +1/-0
Core / Inner Shield |  |  | Measure capacitance between triaxial core and inner shield. | [18 empty] | See table |  |  | Capacitance meter
Core / Tab |  |  | Measure capacitance between triaxial core and ground tab (red). | [18 empty] | See table |  |  | Capacitance meter
LIN |  |  | Measure continuity from LIN mounting screws to stator frame. Ensure that measuring points are free of contaminants (paint etc.) | [18 empty] | Less than 1 ohm |  |  | Fluke meter
Tab |  |  | Disconnect triaxial ground tab from LIN module and measure continuity between ground tab and stator frame. Ensure that measuring points are free of contaminants (paint etc.) | [18 empty] | Less than 1 ohm |  |  | Fluke meter
Shield Inner / Outer |  |  | Measure continuity from inner shield to outer shield. | [18 empty] | Open |  |  | Fluke meter
Shield Location |  |  | Shield connected at M12 connector or terminal block (TB) | [18 empty] | N/A |  |  | Visual
Shim |  |  | Note if shims are used to clear the wedge. | [18 empty] | N/A |  |  | N/A
At ZOOM Cabinet | [21 empty] | Limits |  |  | Tool
ZPU |  |  | Sensor is wired to this ZPU and channel. | [18 empty] | N/A |  |  | N/A
Current mA |  |  | Measure the signal output from LIN module and record value at the ZOOM cabinet. | [18 empty] | Min 4 mA +0/-0.5 |  |  | Fluke meter
Max 20 mA +1/-0
Status |  |  | State of measuring chain after installation and tests. | [18 empty] | N/A |  |  | N/A
Status |  |  | State of measuring chain after installation and tests. | [18 empty] | N/A |  |  | N/A
ZOOM CONFIG |  |  | Choose the apporiate sensor selected in ZOOM CONFIG | [18 empty] | N/A |  |  | N/A
Input Module |  |  | Choose the apporiate input module installed in the ZPU and selected in ZOOM CONFIG | [18 empty] | N/A |  |  | N/A