## PES
PES MEASURING CHAINS | [7 empty] | Project: | [11 empty] | Unit:
[6 empty] | Service nb : | [6 empty] | Service nb :
Item | WME | OUT OF BOX |  |  |  | AT INSTALLATION | [6 empty] | AT ZOOM CABINET
|  | PES Sensor |  |  |  | Grounding |  | Calibration |  | Adjustment |  | Bearing | ZPU |  |  | Verification |  |  | Signal Cable |  |  | Status | ZOOM CONFIG
[6 empty] | (Ω) |  | Calibration sheet
|  | Location | Angle | Serial Number | VSM PRODUCT NUMBER | Sensor / Bracket | Bracket / Frame | Min | Max | mA | Gap | Isolated | ID | Channel | Input Module | Output (mA) | ZOOM | Zero Offset | Shield (M12 / TB) |  | Cable TAG
1
2
3
4
5
6
7
8
9
10
11
12
NOTES | [12 empty] | OBSERVATIONS
1. | Serial numbers to be recorded at time of installation.
2. | Locations and angles to be recorded at time of installation.
3. | Grounding measurements to be done at sensor / bracket locations during installation / commissioning.
4. | Calibration tests (Min & Max) at each sensor location on actual shaft material is done at time of installation; final calibration verified with ZOOM system; enter ‘zero’ offset value.
5. | ZPU ID and Channel to be recorded at commissioning.
6. | Shield location: at M12 connector end or terminal block end in cabinet.
7. | For limits, refer to previous page.
Limits & Measuring Method
General | [17 empty] | Limits |  |  | Tool
Item |  | Sequential number | [15 empty] | N/A |  |  | N/A
WME |  | Sensor is wired to this junction box. | [15 empty] | N/A |  |  | N/A
Out of the Box | [17 empty] | Limits |  |  | Tool
Serial Number |  | Sensor serial number | [15 empty] | N/A |  |  | N/A
Angle |  | Angular position of the sensor | [15 empty] | N/A |  |  | N/A
Location |  | Location of the the sensor in the Unit (UGB, LGB, TGB, etc.) | [15 empty] | N/A |  |  | N/A
At Installation | [17 empty] | Limits |  |  | Tool
Sensor / Bracket |  | Measure continuity from sensor body to stator frame. Ensure that measuring points are free of contaminants (paint etc.). | [15 empty] | Less than 1 ohm |  |  | Fluke meter
Sensor / Frame (Isolated) |  | Measure continuity from sensor body to stator frame. Ensure that measuring points are free of contaminants (paint etc.). Shield must be connected from M12 (metallic) connector to acquisition unit. | [15 empty] | Infinite (open) |  |  | Fluke meter
Sensor / Frame (Non-Isolated) |  | Measure continuity from sensor body to stator frame. Ensure that measuring points are free of contaminants (paint etc.). If M12 connector is plastic, shield must be connected to acquisition unit (ZPU). If M12 connector is metallic, shield must NOT be connected to acquisition unit. | [15 empty] | Less than 1 ohm |  |  | Fluke meter
Min / Max |  | Record values as per calibration sheet. Values are inserted in ZOOM configuration. | [15 empty] | Min / Max |  |  | Excel spreadsheet
mA |  | Measure the signal output from sensor after adjustement and record value. | [15 empty] | ≈12mA |  |  | Fluke meter
Gap |  | Set gap with known feeler gauge and record current measurement. | [15 empty] | sensor middle range |  |  | Feeler gauge
At ZOOM Cabinet | [17 empty] | Limits |  |  | Tool
ZPU |  | Sensor is wired to this ZPU and channel. | [15 empty] | N/A |  |  | N/A
Current mA |  | Measure the signal input in TBP. Should be the same as installed | [15 empty] | Min 4 mA +0/-0.5 |  |  | Fluke meter
Max 20 mA +1/-0
Shield Location |  | Shield connected at M12 connector or terminal block (TB) | [15 empty] | N/A |  |  | Visual
Status |  | State of measuring chain after installation and tests. | [15 empty] | N/A |  |  | N/A
Zero offset |  | Record the offset if it is applied | [15 empty] | N/A |  |  | N/A