## Synchro-Hydro
SYNCHRONIZATION PROBE MEASURING CHAIN |  |  |  | Project: | [10 empty] | Unit:
Item | Location | OUT OF THE BOX |  | AT INSTALLATION | [10 empty] | AT ZOOM CABINET
|  | Sensor |  | Tests | [10 empty] | Terminal Block |  | EXT | Status
|  | Angle | Serial Number | Voltage | LED Blink |  | Taget passage duration | [6 empty] | Target position | Shield | Sync 1 / 2 | Cable TAG
|  |  |  | +24 | Sensor | Ctrl module | Shaft D | Shaft C | Nominal Speed | Max Speed | # of targets | Passage duration (D) | Passage duration (C) | Left / Right
1
2
NOTES | [5 empty] | OBSERVATIONS
1. Always install the 2 targets next to each other for a longer signal.
2. Serial numbers to be recorded at time of installation.
3. Locations and angles to be recorded at time of installation.
4. ZPU ID and Channel to be recorded at commissioning.
5. Shield location: at terminal block end in cabinet.
6. For limits, refer to table above.
Table Limits & Measuring Method
Tests | [16 empty] | Limits | Tool
Voltage |  | Measure voltage at sensor connector between the blue and brown wires. | [14 empty] | 24Vdc +/- 1Vdc | Multimeter
LED blink at sensor |  | While sensor is powered, swipe a small metallic piece in front of sensor. Verify that the internal led blinks with each passage of the metallic piece. | [14 empty] | Led blinks | N/A
LED blink at ZPU |  | While sensor is powered, have a co-worker swipe a small metallic piece in front of sensor. Verify that the ZPU control module green led blinks with each passage of the metallic piece. | [14 empty] | Led blinks | N/A
Target passage duration |  | Find in drawings the shaft diameter (D) or Mesure de shaft cicunference (C). Input the nominal speed, and determine how many targets are required. Note: C=3.1416*D | [14 empty] | >0.5 ms
Shield |  | To be connected at the ZOOM cabinet terminal block only | [14 empty] | N/A | N/A